- Unit Heater Sequence of Operation

- Run Conditions - Scheduled:
The unit shall run according to a user definable time schedule in the following modes:

  - Occupied Mode: The unit shall maintain a heating setpoint of 70°F (adj.).

  - Unoccupied Mode (night setback): The unit shall maintain a heating setpoint of 65°F (adj.).

- Alarms shall be provided as follows:

  - Low Zone Temp: If the zone temperature is less than the heating setpoint by a user definable amount (adj.).

- Demand Limiting - Zone Setpoint Optimization:
To lower power consumption, the zone setpoints shall automatically relax when the facility power consumption exceeds definable thresholds. The amount of relaxation shall be individually configurable for each zone. The zone setpoints shall automatically return to their previous settings when the facility power consumption drops below the thresholds.

- Zone Setpoint Adjust:
The occupant shall be able to adjust the zone temperature heating and cooling setpoints at the zone sensor.

- Zone Optimal Start:
The unit shall use an optimal start algorithm for morning start-up. This algorithm shall minimize the unoccupied warm-up or cool-down period while still achieving comfort conditions by the start of scheduled occupied period.

- Zone Unoccupied Override:
A timed local override control shall allow an occupant to override the schedule and place the unit into an occupied mode for an adjustable period of time. At the expiration of this time, control of the unit shall automatically return to the schedule.

- Fan:
The fan shall run anytime the zone temperature drops below heating setpoint, unless shutdown on safeties.

- Heating Coil Valve:
The controller shall measure the zone temperature and modulate the heating coil valve to maintain its heating setpoint.

- The heating shall be enabled whenever:

  - Outside air temperature is less than 65°F (adj.).

  - AND the zone temperature is below heating setpoint.

  - AND the fan is on.

- Discharge Air Temperature:
The controller shall monitor the discharge air temperature.

- Alarms shall be provided as follows:

  - High Discharge Air Temp: If the discharge air temperature is greater than 120°F (adj.).

  - Low Discharge Air Temp: If the discharge air temperature is less than 40°F (adj.).

- Fan Status:
The controller shall monitor the fan status.

- Alarms shall be provided as follows:

  - Fan Failure: Commanded on, but the status is off.

  - Fan in Hand: Commanded off, but the status is on.

  - Fan Runtime Exceeded: Fan status runtime exceeds a user definable limit (adj.).

- Filter Hours:
The controller shall monitor the fan runtime.

- Alarms shall be provided as follows:

  - Filter Change Required: Filter has been in use for more than 2200 hrs (adj.).

|  | Hardware Points |  |  |  | Software Points |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Point Name | AI | AO | BI | BO | AV | BV | Sched | Trend | Alarm | Show On Graphic |
| Zone Temp | × |  |  |  |  |  |  | × |  | × |
| Zone Setpoint Adjust | × |  |  |  |  |  |  |  |  | × |
| Discharge Air Temp | × |  |  |  |  |  |  | × |  | × |
| Heating Valve |  | × |  |  |  |  |  | × |  | × |
| Zone Override |  |  | × |  |  |  |  | × |  | × |
| Fan Status |  |  | × |  |  |  |  | × |  | × |
| Fan Start/Stop |  |  |  | × |  |  |  | × |  | × |
| Schedule |  |  |  |  |  |  | × |  |  |  |
| Heating Setpoint |  |  |  |  |  |  |  | × |  | × |
| Low Zone Temp |  |  |  |  |  |  |  |  | × |  |
| High Discharge Air Temp |  |  |  |  |  |  |  |  | × |  |
| Low Discharge Air Temp |  |  |  |  |  |  |  |  | × |  |
| Fan Failure |  |  |  |  |  |  |  |  | × |  |
| Fan in Hand |  |  |  |  |  |  |  |  | × |  |
| Fan Runtime Exceeded |  |  |  |  |  |  |  |  | × |  |
| Filter Change Required |  |  |  |  |  |  |  |  | × | × |
| Totals | 3 | 1 | 2 | 1 | 0 | 0 | 1 | 7 | 7 | 9 |
| Total Hardware ( 7 ) |  |  |  |  | Total Software ( 15 ) |  |  |  |  |  |

- Point Summary

|  |  | Hardware Points |  |  |  | Software Points |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Equipment Name | Qty | AI | AO | BI | BO | AV | BV | Sched | Trend | Alarm | Show On Graphic |
| Unit Heater (Typical of 1) | Each | 3 | 1 | 2 | 1 | 0 | 0 | 1 | 7 | 7 | 9 |
|  | Total (x1) | 3 | 1 | 2 | 1 | 0 | 0 | 1 | 7 | 7 | 9 |
| Project Totals |  | 3 | 1 | 2 | 1 | 0 | 0 | 1 | 7 | 7 | 9 |
| Total Hardware ( 7 ) |  |  |  |  |  | Total Software ( 15 ) |  |  |  |  |  |

- APPENDIX B: Glossary of Terms

Control Terms used within the Sequences of Operation:

- adj.

- Adjustable by the end user, through the supplied user interface.

- AI, AO, etc. (Column Headings on Points List)

- AI = Analog Input. A physical input to the control module. 
AO = Analog Output. A physical output from the control module. 
AV = Analog Value. An intermediate (software) point that may be editable or read-only. Editable AVs are typically used to allow the user to set a fixed control parameter, such as a setpoint. Read Only AVs are typically used to display the status of a control operation. 
BI = Binary Input. A physical input to the control module. 
BO = Binary Output. A physical output from the control module. 
BV = Binary Value. An intermediate (software) point that may be editable or read-only. Editable BVs are typically used to allow the user to set a fixed control parameter, such as a setpoint. Read Only BVs are typically used to display the status of a control operation. 
Sched = Schedule. The control algorithm for this equipment shall include a user editable schedule. 
Trend. The control system shall be configured to collect and display a trend log of this object. The trending interval shall be no less than one sample every 5 minutes. (Change of Value trending, where a sample is taken every time the value changes by more than a user-defined minimum, is an acceptable alternative.) 
Alarm. The control system shall be configured to generate an alarm when this object exceeds user definable limits, as described in the Sequence of Controls. 

Note: If the specifications require use of the BACnet protocol, all of the above shall be provided as BACnet objects.

- KW Demand Limiting: *

- An energy management strategy that reduces energy consumption when a system's electric power meter exceeds an operator-defined threshold.

- When power consumption exceeds defined levels, the system automatically adjust setpoints, de-energizes low priority equipment, and takes other pre-programmed actions to avoid peak demand charges. As the demand drops, the system restores loads in a predetermined manner.

- Occupant Override Switch, or Timed Local Override:

- A control option that allows building occupants to override the programmed HVAC schedule for a limited period of time.

- When the override time expires, the zone returns to its unoccupied state.

- Occupant Setpoint Adjustment:

- A control option that allows building occupants to adjust - within limits set by the HVAC control system - the heating and cooling setpoints of selected zones. Typically the user interface for this function is built into the zone sensor.

- Optimal Start-Up: *

- A control strategy that automatically starts an HVAC system at the latest possible time yet ensures comfort conditions by the time the building becomes occupied.

- In a typical implementation, a controller measures the temperature of the zone and the outside air. Then, using design heating or cooling capacity at the design outside air temperature, the system computes how long a unit must run at maximum capacity to bring the zone temperature to its occupied setpoint.

- The optimal start algorithm often includes a self-learning feature to adjust for variations from design capacity.

- A distributed system must use Run on Request with Optimal Start. (See below.)

- Requested, or Run on Request: *

- A control strategy that optimizes the runtime of a source piece of equipment that supplies one or more receiving units - such as an air handler unit supplying zone terminal units with heating, cooling, ventilation, or similar service. Source equipment runs only when needed, not on a fixed schedule.

- The source equipment runs when one or more receiving units request its services. An operator determines how many requests are required to start the source equipment.

- For example, if all the zones in a building are unoccupied and the zone terminal units do not need heating or cooling, the AHU will shut down. However, if a zone becomes occupied or needs cooling, the terminal unit will send a run request to the AHU to initiate the start-up sequence. If this AHU depends on a central chiller, it can send a run request to the chiller.

- The run on request algorithm also allows an operator to schedule occupancy for individual zones based on the needs of the occupants without having to adjust the schedules of related AHUs and chillers.

- Trim and Respond, or Setpoint Optimization: *

- A control strategy that optimizes the setpoint of a source piece of equipment that supplies one or more receiving units - such as an air handler unit supplying zone terminal units with heating, cooling, ventilation, or similar service.

- The source unit communicates with receiving units to determine heating, cooling, and other requirements, and then adjusts its setpoint.

- For example, if all zones are comfortable and do not request cooling, the AHU will gradually increase (trim) its supply air setpoint. When a zone requests cooling, the AHU responds by dropping its setpoint. The more zones that request cooling, the more it drops the setpoint. The AHU repeats this process throughout the day to keep zones cool, but with a supply air setpoint that is no cooler than necessary.

Contracting Terms:

- Furnished or Provided:

- The act of supplying a device or piece of equipment as required meeting the scope of work specified and making that device or equipment operational. All costs required to furnish the specified device or equipment and make it operational are borne by the division specified to be responsible for providing the device or equipment.

- Install or Installed:

- The physical act of mounting, piping or wiring a device or piece of equipment in accordance with the manufacturer's instructions and the scope of work as specified. All costs required to complete the installation are borne by the division specified to include labor and any ancillary materials.

- Interface:

- The physical device required to provide integration capabilities from an equipment vendor's product to the control system. The equipment vendor most normally furnishes the interface device. An example of an interface is the chilled water temperature reset interface card provided by the chiller manufacturer in order to allow the control system to integrate the chilled water temperature reset function into the control system.

- Integrate:

- The physical connections from a control system to all specified equipment through an interface as required to allow the specified control and monitoring functions of the equipment to be performed via the control system.

- * Energy saving option that may not be a standard feature for all vendors, and which may be implemented differently by those vendors who support it.