- VAV Terminal Unit - parallel fan - hw reheat

- Run Conditions - Scheduled:
The unit shall run according to a user definable time schedule in the following modes:

  - Occupied Mode: The unit shall maintain

    - A 74°F (adj.) cooling setpoint

    - A 70°F (adj.) heating setpoint.

  - Unoccupied Mode (night setback): The unit shall maintain

    - A 85°F (adj.) cooling setpoint.

    - A 55°F (adj.) heating setpoint.

- Alarms shall be provided as follows:

  - High Zone Temp: If the zone temperature is greater than the cooling setpoint by a user definable amount (adj.).

  - Low Zone Temp: If the zone temperature is less than the heating setpoint by a user definable amount (adj.).

- Demand Limiting - Zone Setpoint Optimization:
To lower power consumption, the zone setpoints shall automatically relax when the facility power consumption exceeds definable thresholds. The amount of relaxation shall be individually configurable for each zone. The zone setpoints shall automatically return to their previous settings when the facility power consumption drops below the thresholds.

- Zone Setpoint Adjust:
The occupant shall be able to adjust the zone temperature heating and cooling setpoints at the zone sensor.

- Zone Optimal Start:
The unit shall use an optimal start algorithm for morning start-up. This algorithm shall minimize the unoccupied warm-up or cool-down period while still achieving comfort conditions by the start of scheduled occupied period.

- Zone Unoccupied Override:
A timed local override control shall allow an occupant to override the schedule and place the unit into an occupied mode for an adjustable period of time. At the expiration of this time, control of the unit shall automatically return to the schedule.

- Reversing Variable Volume Terminal Unit - Flow Control:
The unit shall maintain zone setpoints by controlling the air flow through one of the following:

- Occupied:

  - When zone temperature is greater than its cooling setpoint, the zone damper shall modulate between the minimum occupied airflow (adj.) and the maximum cooling air flow (adj.) until the zone is satisfied.

  - When the zone temperature is between the cooling setpoint and the heating setpoint, the zone damper shall maintain the minimum required zone ventilation (adj.).

  - When zone temperature is less than its heating setpoint, the controller shall enable heating to maintain the zone temperature at its heating setpoint. Additionally, if warm air is available from the AHU, the zone damper shall modulate between the minimum occupied air flow (adj.) and the maximum heating airflow (adj.) until the zone is satisfied.

- Unoccupied:

  - When the zone is unoccupied the zone damper shall control to its minimum unoccupied air flow (adj.).

  - When the zone temperature is greater than its cooling setpoint, the zone damper shall modulate between the minimum unoccupied air flow (adj.) and the maximum cooling air flow (adj.) until the zone is satisfied.

  - When zone temperature is less than its unoccupied heating setpoint, the controller shall enable heating to maintain the zone temperature at the setpoint. Additionally, if warm air is available from the AHU, the zone damper shall modulate between the minimum unoccupied air flow (adj.) and the auxiliary heating air flow (adj.) until the zone is satisfied.

- Fan Control - Parallel:
The fan shall run whenever the zone controller calls for heat. The fan shall run for a minimum user definable time (adj.).

- Reheating Coil Valve:
The controller shall measure the zone temperature and modulate the reheating coil valve open on dropping temperature to maintain its heating setpoint.

- Discharge Air Temperature:
The controller shall monitor the discharge air temperature.

- Alarms shall be provided as follows:

  - High Discharge Air Temp: If the discharge air temperature is greater than 120°F (adj.).

  - Low Discharge Air Temp: If the discharge air temperature is less than 40°F (adj.).

- Fan Status Feedback:
The fan status shall be monitored.

- Alarms shall be provided as follows:

  - Fan Failure: Commanded on, but the status is off.

  - Fan in Hand: Commanded off, but the status is on.

- Filter Hours:
The controller shall monitor the fan runtime.

- Alarms shall be provided as follows:

  - Filter Change Required: Filter has been in use for more than 2200 hrs (adj.).

|  | Hardware Points |  |  |  | Software Points |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Point Name | AI | AO | BI | BO | AV | BV | Sched | Trend | Alarm | Show On Graphic |
| Zone Temp | × |  |  |  |  |  |  | × |  | × |
| Zone Setpoint Adjust | × |  |  |  |  |  |  |  |  | × |
| Air Flow | × |  |  |  |  |  |  | × |  | × |
| Discharge Air Temp | × |  |  |  |  |  |  | × |  | × |
| Zone Damper |  | × |  |  |  |  |  |  |  | × |
| Reheating Valve |  | × |  |  |  |  |  | × |  | × |
| Zone Override |  |  | × |  |  |  |  | × |  | × |
| Fan Status |  |  | × |  |  |  |  | × |  | × |
| Fan Start/Stop |  |  |  | × |  |  |  |  |  | × |
| Air Flow Setpoint |  |  |  |  | × |  |  | × |  | × |
| Heating Mode |  |  |  |  |  | × |  | × |  |  |
| Schedule |  |  |  |  |  |  | × |  |  |  |
| Heating Setpoint |  |  |  |  |  |  |  | × |  | × |
| Cooling Setpoint |  |  |  |  |  |  |  | × |  | × |
| High Zone Temp |  |  |  |  |  |  |  |  | × |  |
| Low Zone Temp |  |  |  |  |  |  |  |  | × |  |
| High Discharge Air Temp |  |  |  |  |  |  |  |  | × |  |
| Low Discharge Air Temp |  |  |  |  |  |  |  |  | × |  |
| Fan Failure |  |  |  |  |  |  |  |  | × |  |
| Fan in Hand |  |  |  |  |  |  |  |  | × |  |
| Filter Change Required |  |  |  |  |  |  |  |  | × | × |
| Totals | 4 | 2 | 2 | 1 | 1 | 1 | 1 | 10 | 7 | 13 |
| Total Hardware ( 9 ) |  |  |  |  | Total Software ( 20 ) |  |  |  |  |  |