- Single Zone Unit Sequence of Operation

- Run Conditions - Scheduled:
The unit shall run according to a user definable time schedule in the following modes:

  - Occupied Mode: The unit shall maintain

    - A 74°F (adj.) cooling setpoint

    - A 70°F (adj.) heating setpoint.

  - Unoccupied Mode (night setback): The unit shall maintain

    - A 85°F (adj.) cooling setpoint.

    - A 55°F (adj.) heating setpoint.

- Alarms shall be provided as follows:

  - High Zone Temp: If the zone temperature is greater than the cooling setpoint by a user definable amount (adj.).

  - Low Zone Temp: If the zone temperature is less than the heating setpoint by a user definable amount (adj.).

- Demand Limiting - Zone Setpoint Optimization:
To lower power consumption, the zone setpoints shall automatically relax when the facility power consumption exceeds definable thresholds. The amount of relaxation shall be individually configurable for each zone. The zone setpoints shall automatically return to their previous settings when the facility power consumption drops below the thresholds.

- Zone Setpoint Adjust:
The occupant shall be able to adjust the zone temperature heating and cooling setpoints at the zone sensor.

- Zone Optimal Start:
The unit shall use an optimal start algorithm for morning start-up. This algorithm shall minimize the unoccupied warm-up or cool-down period while still achieving comfort conditions by the start of scheduled occupied period.

- Zone Unoccupied Override:
A timed local override control shall allow an occupant to override the schedule and place the unit into an occupied mode for an adjustable period of time. At the expiration of this time, control of the unit shall automatically return to the schedule.

- Freeze Protection:
The unit shall shut down and generate an alarm upon receiving a freezestat status.

- Supply Air Smoke Detection:
The unit shall shut down and generate an alarm upon receiving a supply air smoke detector status.

- Supply Fan:
The supply fan shall run anytime the unit is commanded to run, unless shutdown on safeties. To prevent short cycling, the supply fan shall have a user definable (adj.) minimum runtime.

Alarms shall be provided as follows:

  - Supply Fan Failure: Commanded on, but the status is off.

  - Supply Fan in Hand: Commanded off, but the status is on.

  - Supply Fan Runtime Exceeded: Status runtime exceeds a user definable limit (adj.).

- Cooling Stages:
The controller shall measure the zone temperature and stage the cooling to maintain its cooling setpoint. To prevent short cycling, there shall be a user definable (adj.) delay between stages, and each stage shall have a user definable (adj.) minimum runtime.

- The cooling shall be enabled whenever:

  - Outside air temperature is greater than 60°F (adj.).

  - AND the economizer (if present) is disabled or fully open.

  - AND the zone temperature is above cooling setpoint.

  - AND the supply fan status is on.

  - AND the heating is not active.

- Gas Heating Stages:
The controller shall measure the zone temperature and stage the heating to maintain its heating setpoint. To prevent short cycling, there shall be a user definable (adj.) delay between stages, and each stage shall have a user definable (adj.) minimum runtime.

- The heating shall be enabled whenever:

  - Outside air temperature is less than 65°F (adj.).

  - AND the zone temperature is below heating setpoint.

  - AND the supply fan status is on.

  - AND the cooling is not active.

- Economizer:
The controller shall measure the zone temperature and modulate the economizer dampers in sequence to maintain a setpoint 2°F less than the zone cooling setpoint. The outside air dampers shall maintain a minimum adjustable position of 20% (adj.) open whenever occupied.

- The economizer shall be enabled whenever:

  - Outside air temperature is less than 65°F (adj.).

  - AND the outside air temperature is less than the return air temperature.

  - AND the supply fan status is on.

- The economizer shall close whenever:

  - Mixed air temperature drops from 45°F to 40°F (adj.).

  - OR on loss of supply fan status.

  - OR the freezestat (if present) is on.

- The outside and exhaust air dampers shall close and the return air damper shall open when the unit is off. If Optimal Start Up is available, the mixed air damper shall operate as described in the occupied mode except that the outside air damper shall modulate to fully closed.

- Minimum Outside Air Ventilation - Carbon Dioxide (CO2) Control:
When in the occupied mode, the controller shall measure the return air CO2 levels and modulate the outside air dampers open on rising CO2 concentrations, overriding normal damper operation to maintain a CO2 setpoint of 750 ppm  (adj.).

- Alarms shall be provided as follows:

  - High Return Air Carbon Dioxide Concentration: If the return air CO2 concentration is greater than 1000 ppm (adj.).

- Mixed Air Temperature:
The controller shall monitor the mixed air temperature and use as required for economizer control (if present) or preheating control (if present).

- Alarms shall be provided as follows:

  - High Mixed Air Temp: If the mixed air temperature is greater than 90°F (adj.).

  - Low Mixed Air Temp: If the mixed air temperature is less than 45°F (adj.).

- Return Air Humidity:
The controller shall monitor the return air humidity and use as required for economizer control (if present) or humidity control (if present).

- Alarms shall be provided as follows:

  - High Return Air Humidity: If the return air humidity is greater than 70% (adj.).

  - Low Return Air Humidity: If the return air humidity is less than 35% (adj.).

- Return Air Temperature:
The controller shall monitor the return air temperature and use as required for economizer control (if present).

- Alarms shall be provided as follows:

  - High Return Air Temp: If the return air temperature is greater than 90°F (adj.).

  - Low Return Air Temp: If the return air temperature is less than 45°F (adj.).

- Supply Air Temperature:
The controller shall monitor the supply air temperature.

- Alarms shall be provided as follows:

  - High Supply Air Temp: If the supply air temperature is greater than 120°F  (adj.).

  - Low Supply Air Temp: If the supply air temperature is less than 45°F  (adj.).

|  | Hardware Points |  |  |  | Software Points |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Point Name | AI | AO | BI | BO | AV | BV | Sched | Trend | Alarm | Show On Graphic |
| Zone Temp | × |  |  |  |  |  |  | × |  | × |
| Zone Setpoint Adjust | × |  |  |  |  |  |  |  |  | × |
| RA Carbon Dioxide PPM | × |  |  |  |  |  |  | × | × | × |
| Mixed Air Temp | × |  |  |  |  |  |  | × |  | × |
| Return Air Humidity | × |  |  |  |  |  |  | × |  | × |
| Return Air Temp | × |  |  |  |  |  |  | × |  | × |
| Supply Air Temp | × |  |  |  |  |  |  | × |  | × |
| Mixed Air Dampers |  | × |  |  |  |  |  | × |  | × |
| Zone Override |  |  | × |  |  |  |  | × |  | × |
| Freezestat |  |  | × |  |  |  |  | × | × | × |
| Supply Air Smoke Detector |  |  | × |  |  |  |  | × | × | × |
| Supply Fan Status |  |  | × |  |  |  |  | × |  | × |
| Supply Fan Start/Stop |  |  |  | × |  |  |  | × |  | × |
| Cooling Stage 1 |  |  |  | × |  |  |  | × |  | × |
| Cooling Stage 2 |  |  |  | × |  |  |  | × |  | × |
| Cooling Stage 3 |  |  |  | × |  |  |  | × |  | × |
| Cooling Stage 4 |  |  |  | × |  |  |  | × |  | × |
| Heating Stage 1 |  |  |  | × |  |  |  | × |  | × |
| Heating Stage 2 |  |  |  | × |  |  |  | × |  | × |
| Economizer Zone Temp Setpoint |  |  |  |  | × |  |  | × |  | × |
| RA Carbon Dioxide PPM Setpoint |  |  |  |  | × |  |  | × |  | × |
| Schedule |  |  |  |  |  |  | × |  |  |  |
| Heating Setpoint |  |  |  |  |  |  |  | × |  | × |
| Cooling Setpoint |  |  |  |  |  |  |  | × |  | × |
| High Zone Temp |  |  |  |  |  |  |  |  | × |  |
| Low Zone Temp |  |  |  |  |  |  |  |  | × |  |
| Supply Fan Failure |  |  |  |  |  |  |  |  | × |  |
| Supply Fan in Hand |  |  |  |  |  |  |  |  | × |  |
| Supply Fan Runtime Exceeded |  |  |  |  |  |  |  |  | × |  |
| Compressor Runtime Exceeded |  |  |  |  |  |  |  |  | × |  |
| High RA Carbon Dioxide Concentration |  |  |  |  |  |  |  |  | × |  |
| High Mixed Air Temp |  |  |  |  |  |  |  |  | × |  |
| Low Mixed Air Temp |  |  |  |  |  |  |  |  | × |  |
| High Return Air Humidity |  |  |  |  |  |  |  |  | × |  |
| Low Return Air Humidity |  |  |  |  |  |  |  |  | × |  |
| High Return Air Temp |  |  |  |  |  |  |  |  | × |  |
| Low Return Air Temp |  |  |  |  |  |  |  |  | × |  |
| High Supply Air Temp |  |  |  |  |  |  |  |  | × |  |
| Low Supply Air Temp |  |  |  |  |  |  |  |  | × |  |
| Totals | 7 | 1 | 4 | 7 | 2 | 0 | 1 | 22 | 18 | 23 |
| Total Hardware ( 19 ) |  |  |  |  | Total Software ( 43 ) |  |  |  |  |  |

- Point Summary

|  |  | Hardware Points |  |  |  | Software Points |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Equipment Name | Qty | AI | AO | BI | BO | AV | BV | Sched | Trend | Alarm | Show On Graphic |
| Single Zone Unit (Typical of 1) | Each | 7 | 1 | 4 | 7 | 2 | 0 | 1 | 22 | 18 | 23 |
|  | Total (x1) | 7 | 1 | 4 | 7 | 2 | 0 | 1 | 22 | 18 | 23 |
| Project Totals |  | 7 | 1 | 4 | 7 | 2 | 0 | 1 | 22 | 18 | 23 |
| Total Hardware ( 19 ) |  |  |  |  |  | Total Software ( 43 ) |  |  |  |  |  |

- APPENDIX B: Glossary of Terms

Control Terms used within the Sequences of Operation:

- adj.

- Adjustable by the end user, through the supplied user interface.

- AI, AO, etc. (Column Headings on Points List)

- AI = Analog Input. A physical input to the control module. 
AO = Analog Output. A physical output from the control module. 
AV = Analog Value. An intermediate (software) point that may be editable or read-only. Editable AVs are typically used to allow the user to set a fixed control parameter, such as a setpoint. Read Only AVs are typically used to display the status of a control operation. 
BI = Binary Input. A physical input to the control module. 
BO = Binary Output. A physical output from the control module. 
BV = Binary Value. An intermediate (software) point that may be editable or read-only. Editable BVs are typically used to allow the user to set a fixed control parameter, such as a setpoint. Read Only BVs are typically used to display the status of a control operation. 
Sched = Schedule. The control algorithm for this equipment shall include a user editable schedule. 
Trend. The control system shall be configured to collect and display a trend log of this object. The trending interval shall be no less than one sample every 5 minutes. (Change of Value trending, where a sample is taken every time the value changes by more than a user-defined minimum, is an acceptable alternative.) 
Alarm. The control system shall be configured to generate an alarm when this object exceeds user definable limits, as described in the Sequence of Controls. 

Note: If the specifications require use of the BACnet protocol, all of the above shall be provided as BACnet objects.

- KW Demand Limiting: *

- An energy management strategy that reduces energy consumption when a system's electric power meter exceeds an operator-defined threshold.

- When power consumption exceeds defined levels, the system automatically adjust setpoints, de-energizes low priority equipment, and takes other pre-programmed actions to avoid peak demand charges. As the demand drops, the system restores loads in a predetermined manner.

- Occupant Override Switch, or Timed Local Override:

- A control option that allows building occupants to override the programmed HVAC schedule for a limited period of time.

- When the override time expires, the zone returns to its unoccupied state.

- Occupant Setpoint Adjustment:

- A control option that allows building occupants to adjust - within limits set by the HVAC control system - the heating and cooling setpoints of selected zones. Typically the user interface for this function is built into the zone sensor.

- Optimal Start-Up: *

- A control strategy that automatically starts an HVAC system at the latest possible time yet ensures comfort conditions by the time the building becomes occupied.

- In a typical implementation, a controller measures the temperature of the zone and the outside air. Then, using design heating or cooling capacity at the design outside air temperature, the system computes how long a unit must run at maximum capacity to bring the zone temperature to its occupied setpoint.

- The optimal start algorithm often includes a self-learning feature to adjust for variations from design capacity.

- A distributed system must use Run on Request with Optimal Start. (See below.)

- Requested, or Run on Request: *

- A control strategy that optimizes the runtime of a source piece of equipment that supplies one or more receiving units - such as an air handler unit supplying zone terminal units with heating, cooling, ventilation, or similar service. Source equipment runs only when needed, not on a fixed schedule.

- The source equipment runs when one or more receiving units request its services. An operator determines how many requests are required to start the source equipment.

- For example, if all the zones in a building are unoccupied and the zone terminal units do not need heating or cooling, the AHU will shut down. However, if a zone becomes occupied or needs cooling, the terminal unit will send a run request to the AHU to initiate the start-up sequence. If this AHU depends on a central chiller, it can send a run request to the chiller.

- The run on request algorithm also allows an operator to schedule occupancy for individual zones based on the needs of the occupants without having to adjust the schedules of related AHUs and chillers.

- Trim and Respond, or Setpoint Optimization: *

- A control strategy that optimizes the setpoint of a source piece of equipment that supplies one or more receiving units - such as an air handler unit supplying zone terminal units with heating, cooling, ventilation, or similar service.

- The source unit communicates with receiving units to determine heating, cooling, and other requirements, and then adjusts its setpoint.

- For example, if all zones are comfortable and do not request cooling, the AHU will gradually increase (trim) its supply air setpoint. When a zone requests cooling, the AHU responds by dropping its setpoint. The more zones that request cooling, the more it drops the setpoint. The AHU repeats this process throughout the day to keep zones cool, but with a supply air setpoint that is no cooler than necessary.

Contracting Terms:

- Furnished or Provided:

- The act of supplying a device or piece of equipment as required meeting the scope of work specified and making that device or equipment operational. All costs required to furnish the specified device or equipment and make it operational are borne by the division specified to be responsible for providing the device or equipment.

- Install or Installed:

- The physical act of mounting, piping or wiring a device or piece of equipment in accordance with the manufacturer's instructions and the scope of work as specified. All costs required to complete the installation are borne by the division specified to include labor and any ancillary materials.

- Interface:

- The physical device required to provide integration capabilities from an equipment vendor's product to the control system. The equipment vendor most normally furnishes the interface device. An example of an interface is the chilled water temperature reset interface card provided by the chiller manufacturer in order to allow the control system to integrate the chilled water temperature reset function into the control system.

- Integrate:

- The physical connections from a control system to all specified equipment through an interface as required to allow the specified control and monitoring functions of the equipment to be performed via the control system.

- * Energy saving option that may not be a standard feature for all vendors, and which may be implemented differently by those vendors who support it.