- VAV AHU – hw heat - cw cooling - economizer – Sequence of Operation

- Run Conditions - Requested:
The unit shall run whenever:

  - Any zone is occupied.

  - OR a definable number of unoccupied zones need heating or cooling.

- Freeze Protection:
The unit shall shut down and generate an alarm upon receiving a freezestat status.

- High Static Shutdown:
The unit shall shut down and generate an alarm upon receiving an high static shutdown signal.

- Return Air Smoke Detection:
The unit shall shut down and generate an alarm upon receiving a return air smoke detector status.

- Supply Air Smoke Detection:
The unit shall shut down and generate an alarm upon receiving a supply air smoke detector status.

- Supply Fan:
The supply fan shall run anytime the unit is commanded to run, unless shutdown on safeties. To prevent short cycling, the supply fan shall have a user definable (adj.) minimum runtime.

Alarms shall be provided as follows:

  - Supply Fan Failure: Commanded on, but the status is off.

  - Supply Fan in Hand: Commanded off, but the status is on.

  - Supply Fan Runtime Exceeded: Status runtime exceeds a user definable limit (adj.).

- Supply Air Duct Static Pressure Control:
The controller shall measure duct static pressure and shall modulate the supply fan VFD speed to maintain a duct static pressure setpoint of 1.5in H2O (adj.). The supply fan VFD speed shall not drop below 30% (adj.).

- Alarms shall be provided as follows:

  - High Supply Air Static Pressure: If the supply air static pressure is 25% (adj.) greater than setpoint.

  - Low Supply Air Static Pressure: If the supply air static pressure is 25% (adj.) less than setpoint.

  - Supply Fan VFD Fault.

- Supply Air Temperature Setpoint - Optimized:
The controller shall monitor the supply air temperature and shall maintain a supply air temperature setpoint reset based on zone cooling and heating requirements

- The supply air temperature setpoint shall be reset for cooling based on zone cooling requirements as follows:

  - The initial supply air temperature setpoint shall be 55°F (adj.).

  - As cooling demand increases, the setpoint shall incrementally reset down to a minimum of 53°F (adj.).

  - As cooling demand decreases, the setpoint shall incrementally reset up to a maximum of 72°F (adj.) .

- If more zones need heating than cooling, then the supply air temperature setpoint shall be reset for heating as follows:

  - The initial supply air temperature setpoint shall be 82°F (adj.).

  - As heating demand increases, the setpoint shall incrementally reset up to a maximum of 85°F (adj.).

  - As heating demand decreases, the setpoint shall incrementally reset down to a minimum of 72°F (adj.).

- Cooling Coil Valve:
The controller shall measure the supply air temperature and modulate the cooling coil valve to maintain its cooling setpoint.

The cooling shall be enabled whenever:

  - Outside air temperature is greater than 60°F (adj.).

  - AND the economizer (if present) is disabled or fully open.

  - AND the supply fan status is on.

  - AND the heating (if present) is not active.

- The cooling coil valve shall open to 50% (adj.) whenever the freezestat (if present) is on.

- Alarms shall be provided as follows:

  - High Supply Air Temp: If the supply air temperature is 5°F (adj.) greater than setpoint.

- Heating Coil Valve:
The controller shall measure the supply air temperature and modulate the heating coil valve to maintain its heating setpoint.

- The heating shall be enabled whenever:

  - Outside air temperature is less than 65°F (adj.).

  - AND the supply fan status is on.

  - AND the cooling (if present) is not active.

- The heating coil valve shall open whenever:

  - Supply air temperature drops from 40°F to 35°F (adj.).

  - OR the freezestat (if present) is on.

- Alarms shall be provided as follows:

  - High Supply Air Temp: If the supply air temperature is greater than 120°F (adj.).

  - Low Supply Air Temp: If the supply air temperature is 5°F (adj.) less than setpoint.

- Economizer:
The controller shall measure the mixed air temperature and modulate the economizer dampers in sequence to maintain a setpoint 2°F (adj.) less than the supply air temperature setpoint. The outside air dampers shall maintain a minimum adjustable position of 20% (adj.) open whenever occupied.

- The economizer shall be enabled whenever:

  - Outside air temperature is less than 65°F (adj.).

  - AND the outside air enthalpy is less than 22Btu/lb (adj.)

  - AND the outside air temperature is less than the return air temperature.

  - AND the outside air enthalpy is less than the return air enthalpy.

  - AND the supply fan status is on.

- The economizer shall close whenever:

  - Mixed air temperature drops from 40°F to 35°F (adj.)

  - OR the freezestat (if present) is on.

  - OR on loss of supply fan status.

- The outside and exhaust air dampers shall close and the return air damper shall open when the unit is off. If Optimal Start Up is available the mixed air damper shall operate as described in the occupied mode except that the outside air damper shall modulate to fully closed.

- Minimum Outside Air Ventilation - Fixed Percentage:
The outside air dampers shall maintain a minimum adjustable position during building occupied hours and be closed during unoccupied hours.

- Mixed Air Temperature:
The controller shall monitor the mixed air temperature and use as required for economizer control (if present) or preheating control (if present).

- Alarms shall be provided as follows:

  - High Mixed Air Temp: If the mixed air temperature is greater than 90°F (adj.).

  - Low Mixed Air Temp: If the mixed air temperature is less than 45°F (adj.).

- Return Air Humidity:
The controller shall monitor the return air humidity and use as required for economizer control (if present) or humidity control (if present).

- Alarms shall be provided as follows:

  - High Return Air Humidity: If the return air humidity is greater than 70% (adj.).

  - Low Return Air Humidity: If the return air humidity is less than 35% (adj.).

- Return Air Temperature:
The controller shall monitor the return air temperature and use as required for setpoint control or economizer control (if present).

- Alarms shall be provided as follows:

  - High Return Air Temp: If the return air temperature is greater than 90°F (adj.).

  - Low Return Air Temp: If the return air temperature is less than 45°F (adj.).

- Supply Air Temperature:
The controller shall monitor the supply air temperature.

- Alarms shall be provided as follows:

  - High Supply Air Temp: If the supply air temperature is greater than 120°F  (adj.).

  - Low Supply Air Temp: If the supply air temperature is less than 45°F  (adj.).

|  | Hardware Points |  |  |  | Software Points |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Point Name | AI | AO | BI | BO | AV | BV | Sched | Trend | Alarm | Show On Graphic |
| Supply Air Static Pressure | × |  |  |  |  |  |  | × | × | × |
| Supply Air Temp | × |  |  |  |  |  |  | × |  | × |
| Mixed Air Temp | × |  |  |  |  |  |  | × |  | × |
| Return Air Humidity | × |  |  |  |  |  |  | × |  | × |
| Return Air Temp | × |  |  |  |  |  |  | × |  | × |
| Supply Air Temp | × |  |  |  |  |  |  | × |  | × |
| Supply Fan VFD Speed |  | × |  |  |  |  |  | × |  | × |
| Cooling Valve |  | × |  |  |  |  |  | × |  | × |
| Heating Valve |  | × |  |  |  |  |  | × |  | × |
| Mixed Air Dampers |  | × |  |  |  |  |  | × |  | × |
| Freezestat |  |  | × |  |  |  |  | × | × | × |
| High Static Shutdown |  |  | × |  |  |  |  | × | × | × |
| Return Air Smoke Detector |  |  | × |  |  |  |  | × | × | × |
| Supply Air Smoke Detector |  |  | × |  |  |  |  | × | × | × |
| Supply Fan VFD Fault |  |  | × |  |  |  |  |  | × | × |
| Supply Fan Status |  |  | × |  |  |  |  | × |  | × |
| Supply Fan Start/Stop |  |  |  | × |  |  |  | × |  | × |
| Supply Air Static Pressure Setpoint |  |  |  |  | × |  |  |  |  | × |
| Supply Air Temp Setpoint |  |  |  |  | × |  |  | × |  | × |
| Economizer Mixed Air Temp Setpoint |  |  |  |  | × |  |  | × |  | × |
| High Supply Air Static Pressure |  |  |  |  |  |  |  |  | × |  |
| Low Supply Air Static Pressure |  |  |  |  |  |  |  |  | × |  |
| Supply Fan Failure |  |  |  |  |  |  |  |  | × |  |
| Supply Fan in Hand |  |  |  |  |  |  |  |  | × |  |
| Supply Fan Runtime Exceeded |  |  |  |  |  |  |  |  | × |  |
| High Supply Air Temp |  |  |  |  |  |  |  |  | × |  |
| Low Supply Air Temp |  |  |  |  |  |  |  |  | × |  |
| High Mixed Air Temp |  |  |  |  |  |  |  |  | × |  |
| Low Mixed Air Temp |  |  |  |  |  |  |  |  | × |  |
| High Return Air Humidity |  |  |  |  |  |  |  |  | × |  |
| Low Return Air Humidity |  |  |  |  |  |  |  |  | × |  |
| High Return Air Temp |  |  |  |  |  |  |  |  | × |  |
| Low Return Air Temp |  |  |  |  |  |  |  |  | × |  |
| High Supply Air Temp |  |  |  |  |  |  |  |  | × |  |
| Low Supply Air Temp |  |  |  |  |  |  |  |  | × |  |
| Totals | 6 | 4 | 6 | 1 | 3 | 0 | 0 | 18 | 21 | 20 |
| Total Hardware ( 17 ) |  |  |  |  | Total Software ( 42 ) |  |  |  |  |  |